Scaffold Inspection Checklist

Date: 						Inspected By:

Location:

| Item # | Scaffold Inspection Checklist | Yes | No | N/A |
| --- | --- | --- | --- | --- |
| 1 | Erection and inspection completed by a competent worker |  |  |  |
| 2 | Scaffold is erected with vertical members plumb and ledgers and bearers level |  |  |  |
| 3 | All scaffold components present, tight and secure |  |  |  |
| 4 | No tubes or members over extended and hazardous |  |  |  |
| 5 | Base plates and screws firmly supported on all legs and mudsills |  |  |  |
| 6 | Levelling adjustment screws extended more than the lesser of two-thirds of its total length or 60 centimetres |  |  |  |
| 7 | Effectively guyed or secured to a building or structure where the height of the scaffold exceeds 3 times its minimum base |  |  |  |
| 8 | Building ties or guys placed at a height not exceeding 3 times the scaffold minimum base dimensions, and at horizontal intervals of every third bay or 6.4m, whichever is lesser, at the end of the scaffold. |  |  |  |
| 9 | Rolling scaffold wheels are locked with outriggers extended to maintain a maximum height of 3 times the smallest base dimensions |  |  |  |
| 10 | Platform planks have cleats on underside at each end with wood/angle iron |  |  |  |
| 11 | Platform planks tied down securely |  |  |  |
| 12 | Platform planks maximum span 3.05m for light duty and 2.13m for heavy duty |  |  |  |
| 13 | Separate ladder(s) used for scaffold access |  |  |  |
| 14 | Ladder(s) securely fastened in place with siderails extending approximately one metre above the uppermost working level |  |  |  |
| 15 | Perimeter placed on work surfaces – toe boards permanent and temporary with dimensions of 2.54cm x 10.16cm |  |  |  |
| 16 | Safety cage around vertical ladders where a potential fall is more than 7.32 metres in length. |  |  |  |
| 17 | Open sides have guard rails with a top rail located 0.9 metres to 1.1 metres above the working surface and an intermediate rail located midway between the top rail and the working surface. |  |  |  |
| 18 | Separate rope or handline in place at all platforms to raise and lower tools or material |  |  |  |
| 19 | Warning devices/signs provided if erected over walkways or roadways |  |  |  |
| 20 | Minimum clearance of 5.5 meters from overhead powerlines is maintained where there is no permit from appropriate utilities |  |  |  |
| 21 | Scaffold constructed and maintained according to certified engineer or manufacturer’s’ specifications or drawings |  |  |  |
| 22 | Inspected daily by a competent worker, tagged at each entry and exit point |  |  |  |

| Item # | Corrective Action Required | Assigned to | Completion date |
| --- | --- | --- | --- |

| Signature of Inspectors: | 1 |
| --- | --- |
| 2. | 3. |